TECHNICAL DATA								”Made in Canada”

CAN\ULC-S 705.1 CCMC 13244-L

# AIR BARRIER CCMC 07273

Polarfoam™ PF-7300-0 SOYA is a thermal insulation spray applied rigid polyurethane foam, peach in colour, that is tested by an independent recognized laboratory.  This foam product surpasses the requirements outlined in CAN/ULC S705.1-01 (Including amendment 1 & 2) “Standard for thermal insulation – Spray applied rigid polyurethane foam, medium density – Material Specification”.

Polarfoam™ PF-7300-0 SOYA material (i.e. the highest LTTR classification) meets the requirements of the National Building code of Canada and is evaluated by the National Research Council Canada under CCMC Listing #13244-L.  Polarfoam™ PF-7300-0 SOYA ecological foam is formulated with recycled plastic material,  renewable soya product, and without any Ozone Depletion Substance blowing agent (Zero ODS).  This product meets all the requirements of the Montreal protocol for ozone layer protection.  Polarfoam™ PF-7300-0 SOYA exceeds the highest requirements for VOC with the GREENGUARD Children and School® certifications.  Polarfoam™ PF-7300-0 SOYA is applied exclusively by licensed installers and contractors under the application standard CAN/ULC S705.2.

#### PHYSICAL PROPERTIES

| Method | Description | Value |  |
| --- | --- | --- | --- |
| ASTM D1622 | Core Density | 34-37 Kg/m³ | 2.1-2.3 lb/ft³ |
| ASTM C518 | Initial Thermal Resistance, .25.4 mm. | 1.26 RSI/25 mm | R 7.2 |
|  | Aged Thermal Resistance, 180 days @ 23°C, 25.4 mm | 1.17 RSI/25 mm | R 6.6 |
| CAN/ULC S770 | CAN/ULC S705.1-01 (amendment 1 & 2) Classification | Classification (LTTR) | Type 2 |
| ASTM D2856 | Open Cells | <1% |  |
| ASTM D 1621 | Compressive Strength (10%) | 195 kPa | 28.3 psi |
| ASTM D1623 | Tensile Strength | 355 kPa | 51.5 psi |
| ASTM D2842 | Volumetric Water Absorption % | 0.8% |  |
| ASTM E96 | Water Vapour Permeance (core), 50 mm | 37 ng/Pa.s.m² | .65 Perm |
| CCMC 07273 | Air Barrier Material, 25-30 mm | 0.00004 L/s/m² @ 75Pa |  |
| CAN/ULC S102 CAN/ULC S101-04 | Flame Spread Classification - Tunnel FSC-1=32 - Corner FSC-2=200 Smoke Develop Index | 200 396 Passed |  |
| ASTM D2126 | Dimensional Stability, 28 days (% Volume Change, sample without skin) -20°C 80°C 70°C, 97% R.H. | -0.03% +2.9% +9.8% |  |
| CAN/ULC S774 | VOC Emissions from polyurethane foam-Occupancy | Conform | 24 hrs. |
| GREENGUARD | Indoor Air Quality® | Certified |  |
| GREENGUARD | Children & Schools® | Certified |  |
| ASTM E-1331 | Colour | Peach |  |
| ASTM C 1338 | Fungi Resistance | No Fungal Growth |  |

#### LIQUID COMPONENTS PROPERTIES

| Property | Isocyanate | Resin |
| --- | --- | --- |
| Colour | Brown | Peach |
| Viscosity @ 25°C | 150-350 cps | 150-350 cps |
| Specific gravity | 1.20-1.24 | 1.20-1.24 |
| Shelf life* | 12 months | 6 months |
| Mixing ratio (volume) | 100 | 100 |
| Vapour pressure @ 25°C | 10-7 psi | 7-9 psi |

Note:  Components system storage temperature recommendation 15-25°C (59-77°F)

*See MSDS for more information

#### MACHINE PROCESSING PARAMETERS USED

| Type of machine | Gusmer H20/35, D Gun, mix chamber #62 |
| --- | --- |
| Components Iso & Resin Temperature | 38°C (100°F) |
| Components Iso & Resin Pressure | 5860-6900 kPa (850-1000psi) |
| Ambient temperature | 23° (73°F) |
| Thickness per pass | 30 mm (1 ¼ inches) |
| Number of passes | 2 |
| Substrate | Polyethylene Board |

#### REACTIVITY PROFILE

| Cream Time | Gel Time | Tack Free Time | End of Rise |
| --- | --- | --- | --- |
| 0-1 sec. | 2-3 sec. | 4-5 sec. | 4-5 sec. |

#### RECOMMENDED PROCESSING CONDITIONS

| Mixing ratio Iso/Resin | 1/1 |
| --- | --- |
| Mixing temperature at the gun | 38°C (100°F) @ 49°C (120°F) |
| Mixing pressure (minimum) | 5516 kPa (800 psi) |
| Substrate & Ambient temperature | > -10°C (14°F) |
| Curing temperature | > -10°C (14°F) |
| Maximum thickness per pass | 50 mm (2 inches) |
| Maximum thickness of successive passes | 100 mm (4 inches) |
| Minimum cooling time period before applying over 4 in. thick application | 4 hours |

#### GENERAL INFORMATION

It is recommended that the foam be covered with an approved thermal barrier in accordance to the local and national building codes when used in buildings and a protective coating when used outside.  This product should not be used when the continuous service temperature of the substrate is outside the range of -60°C to 82°C.

The information herein is to assist customers in determining whether our products are suitable for their applications.  We request that customers inspect and test our products before use and satisfy themselves as to contents and suitability.  Nothing herein shall constitute a warranty, express or implied, including any warranty of merchantability or fitness, nor is protection from any law or patent inferred.  All patent rights are reserved.  The foam product is combustible and must be covered by an approved thermal barrier.  The exclusive remedy for all proven claims is replacement of our materials.

October 28, 2013